## Comments on LCP BREF
Comments from (Forum Member) | Comment number | Chapter No. / section No. (if available) |  |  |  |  | Chapter title (only if there is no section or chapter No.) | Page # (PDF version of the document) | Comment description | Proposal for modification | Rationale
EEB | 1 | 10 |  |  |  |  | Scope | 742 | The definition of "new" combustion plant as it stands has far reaching flaws in terms of practical impact of the revised LCP BREF. | Modify by : "a combustion plant first operated at the installation following the publication of these BAT conclusions or a replacement of a combustion plant on the existing foundations of the installation, or replacement of an installation on the same site which has a technical connection and which could have an effect on emissions and pollution following the publication of these BAT conclusions. The BAT conclusions apply from the date of the publication of these BAT conclusions” | See split view no 3 circulated 21 October 2015. This is of fundamental importance to the EEB. The current formulation allows for potantial abuses by permitting authorities and fundamentally undermines the effectiveness of the LCP BAT standards in practical terms. The proposed modification will also ensure legal consistency with the definitions of what is a new or existing plant by member states • As it stands, the standards for “new plants” will only apply effectively to combustion plants that have been permitted after the publication of the BAT conclusions i.e. not likely prior to Q2 2017 or even later if further delays for publication would occur. This provision effectively promotes the status quo in environmental performance for existing plants (in the sense of energy generation through combustion in installations above a certain threshold) which concerns roughly 98% of all coal/lignite plants for the decades to come • the cut-off date refers to when a “combustion plant” has been permitted which are to be understood as boilers i.e. “Any technical apparatus in which fuels are oxidised in order to use the heat thus generated”. This would mean that the stakholders assume that the only relevant parameter to consider in relation to differentiating the stricter BAT benchmarks (“new” plant standards) from the laxist BAT-C standards (“existing” plants) is the first permit date / and complete replacement date of a boiler/turbine/engine. The precise terms used in these definitions have far reaching consequences in terms of effective environmental performance. A Large Combustion Plant is much more than a boiler and environmental performance is improved by the abatement techniques or other installations at the same site with technical connection which are not themselves defined as “combustion plant” (boiler/engine/turbine). Significant emission reductions are achieved without boiler/engine/turbine change e.g. in case of replacement of abatement installations such as FGD units or systems / new dust filter types which are not themselves defined as a “combustion plant” according to the currently used definition but significantly affect environmental performance of the LCP. The reference to "complete replacement" also raises legal uncertainty on what is meant with this. These elements should be considered since it is the uptake of the level of performance standards that is at stake here. Whilst boiler types and age indeed has implications on performance levels on certain parameters (e.g. NOx formation, energy efficiency) that is clearly not the case for SOx, dust and hg controls or water emissions. We expect that most of the boiler modifications (primary measures) already took place to meet the 2006 LCP BREF. At least that is the case for EU lignite plants
EEB | 2 | 10 |  |  |  |  | Scope | 742 | The definition of "new" combustion unitt as it stands has far reaching flaws in terms of practical impact of the revised LCP BREF. | see above | see above
EEB | 3 | 10 | [6 empty] | Throughout the BAT conclusions: All footnote derogations or relaxations referring to higher values obtained for plants that are existing plants under Chapter III of the IED (whenever the footnote refers to "plants put into operation no later than 7 January 2014" have to be removed, since these constitute an alignment to the IED Annex V Emission Limit Values | DELETE All footnote derogations or relaxations referring to higher values obtained for plants that are existing plants under Chapter III of the IED (whenever the footnote refers to "plants put into operation no later than 7 January 2014" | The footnote derogations are not based on sound technico economic facts. These constitute an "alignment" to the politically agreed lowest common denominator Emission Limit Values (ELVs) set in the IED in 2010, but certainly do not correspond to BAT-AEL. Further these even constitute a worsening of the BAT-AEL (daily averaged) set in the 2006 LCP BREF! The added value and credibility of the practical impact of the revised LCP BREF on existing plants (that is 98% of the portfolio) is questioned if these footnotes are retained under the current definition of a "new plant". The EEB insists that these are removed for all solid fuels in particular coal/lignite. See split view no 6 (21 October 2016) and previous split views submitted on this critical issue.
EEB | 4 | [5 empty] | Scope | 746 | provide a possible definition of 'emergency use' | Add: "Emergency use is defined as a state of the power system that is not normal in accordance with the EU Network Code on Operational Security" | The relaxations are purely arbitrary and not backed up by any technical (and not even economic) facts. It constitutes a sidelining of the agreed derogation procedure foreseen by the IED pursuant to Article 15(4) where the (dis)proportionality of costs compared to the benefits claims for meeting a certain level of emissions is properly weighted by the competent authority given the specific conditions for the installation concerned and subject to public participation. These upfront relaxations based on limited operating hours for existing plants is in our view a distortion of competition in the liberalised energy market. Special treatment should not apply to power generation operating in the liberalised wholesale electricity and balancing markets. Any derogation should be limited to out-of-market emergency conditions.At times of peak energy demand when renewable energy sources are not (sufficiently) available, air quality is more likely to be poor. The derogations / relaxations will create the perverse situation of rewarding the worst performing plants (with exemptions from BAT performance) the Industrial Emissions Directive is trying to avoid (more rationale is provided in the Briefing provided by RAP/EEB to the comments on the Background paper submitted to BATIS 21/05/2015)
EEB | 5 | 10 | [6 empty] | Throughout the BAT conclusions: All footnote derogations or relaxations referring to higher values obtained for plants that are existing plants under Chapter III of the IED (whenever the footnote refers to "plants put into operation no later than 7 January 2014" and /or 'plants put into operation no later than 27 November 2003" have to be removed, since these constitute an alignment to the IED Annex V Emission Limit Values This derogation is arbitrary and not based on sound technico economic facts. It is not more than a Transitional National Plan (TNP) users reward scheme. | Throughout the BAT conclusions: All footnote derogations or relaxations referring to higher values that refer to "plants put into operation no later than 7 January 2014" Option 1 (preferred) : DELETE. Option 2 (backup compromise): Add to the footnotes "[...] subject to prior validation of a derogation pursuant to Article 15(4) of the Industrial Emissions Directive". | Same comment as comment #4. The EEB is confident that NGOs of the countries wanting to make use of this derogation would be ready to accept a compromise through Art 15(4) of the IED. This should be handlled case by case and not undermined through negotiations in the LCP BREF. If "consistency" is indeed seeked for by the COM then it should be with the agreed procedure agreed by the legislator, the current approach is nothing else than a polluters/laggards reward system and has no place in a BAT document.
EEB | 6 | 10 | 2 | 1 | 3 |  |  | 769 | This derogation (footnote 7) is arbitrary and not based on sound technico economic facts. It is not more than a Transitional National Plan (TNP) users reward scheme. Further the EIPPCB has stepped beyond its remit of "consistency" check by extending footnote 7 (page 769) the relaxation to a) lignite fuels and b) other boiler types (fluidised bed boilers) on top of the size threshold. The inital footnote was limited to pulverised combustion boilers and hardcoal only. Poland/EURELECTRIC have asked to extend this to the >300MWth size category, but limiting it to (hard) coal and pulverised combustion "only". The extension is due to new placing of the footnote 7 to the whole of the column. | Footnote 7: Option 1 (preferred) : DELETE. Option 2 (backup compromise): amend as follows: "In the case of coal fired PC plants put into operation no later than 1 July 1987, which are operated <1500h/yr and for which SCR and/or SNCR is not applicable, the higher end of the range is 340mg/Nm, subject to prior validation of a derogation pursuant to Article 15(4) of the Industrial Emissions Directive" | Referring to pre 1987 plants in order to set derogatory BAT-AEL which correspond to "state of the art" post 2021 is not a straightforward approach. In fact it is a reward system for those operators that have evaded BAT since the building of the plant, which currently are into the TNP and which would lilke to have a relaxed retirement scheme post 2021. We think this is at odds with "better regulation" and even more with what the whole BAT exercise is about. Operating up to 1500hours is a lot (too much) giving the future market prospects for these type of plants. Member States which implemented the 2006 LCP BREF made sure that large hardcoal LCPs all operate with an SCR (irrespective of effective hours). These provisions would actually allow to switch off the SCR although investments have been made and rather let dirtiest and oldest plants allowing to run with primary NOx abatement only -up to 340mg/Nm³, instead with higher returns of profit margins. At worst it will create a very profitable retirement scheme for precisely those LCPs that have managed to evade the 2006 LCP BAT standards for decades, when the Transitional National Plan will end (as from mid 2020). That is the case for all except one UK plant, the delegation that requested this relaxation. Rewarding the laggards of the sector cannot be the purpose of the BREF! Further the EIPPCB did accidentally/or on purpose extend the relaxation beyond their remit to also apply to lignite fuels and other than PC boilers: The comment to change was provided by Poland. The proposal was to extend the footnote also to the plant size category <300MWth, however the proposal is limited to coal and does not include lignite fired boilers. There is also a technical reason for this since lignite fired plants / fluidized hardcoal boilers have lower NOx emissions and it is therefore less demanding upon them to meet a given NOx BAT-AEL than it is for coal, in particular PC boilers. As per the comment submitted to the revised draft BAT Conclusion in February 2016, Poland (Michal Chedozko, comment #3) asked the following: Comment description: Footnote (7) should be applicable to all existing coal-fired plants, not only >300MW. Proposal for modification: Add footnote (7) to existing plants column and add word "coal fired" in the footnote - " (7) In the case of coal-fired plants…". It is clear from the comment that the Polish delegation wanted to extend the derogation to the other coal fired boilers <300MWth, but NOT to lignite plants as well. With the new placing of that footnote and its extension of scope the Bureau is –putting aside the <300MWth size category extension- therefore exceeding its remit for addressing inconsistencies in extending the relaxation to include lignite fired boilers/plants as well as including other type of boilers (fluidized hardcoal boilers).
EEB | 7 | 10 | 2 | 1 | 4 |  |  | 771 | Add a requirement that the question of whether this is indeed not possible to meet the standard BAT-AEL for SO2 based on "technico-economic" reasons is subject to a public consultation in accordance to Article 15(4) of the IED. | Preferred option: DELETE the desulphurisation rate text. Proposed compromise new text: "For a combustion plant with a total rated thermal input of more than 300 MWth, which is specifically designed to fire indigenous lignite fuels and which can demonstrate that it cannot achieve the BAT-AELs mentioned in Table 10.5 for techno-economic reasons subject to prior validation of a derogation pursuant to Article 15(4) of the Industrial Emissions Directive, the upper end of the yearly average BAT-AEL range is as follows: | In line with the split views expressed by EEB on the inadequacy of the SO2 BAT-AEL tables (not differentiating in accordance to S content in the fuels as we proposed) we insist that this desulphurisation rate derogation is clearly pre-conditional to the Art 15(4) derogation to be applied under the IED. This should be the standard practice since we are referring clearly to a derogation. The public has its say on what is economically acceptable, espcially since we are referring to the worst types of lignites in terms of sulphur content. The text builds on Article 72(4) point a of the IED. • The relaxations are purely arbitrary and not backed up by any technical (and not even economic) facts • It constitutes a sidelining of the agreed derogation procedure foreseen by the IED pursuant to Article 15(4) where the (dis)proportionality of costs compared to the benefits claims for meeting a certain level of emissions is properly weighted by the competent authority given the specific conditions for the installation concerned and subject to public participation • Further, Article 31 and 72(4) of the IED do not allow a desulphurisation rate derogation based on economic grounds but on technical arguments only • These upfront relaxations for more polluting fuels is in our view a distortion of competition in the liberalised energy market. Special treatment should not apply to power generation operating in the liberalised wholesale electricity and balancing markets, even less for highly polluting fuels. Any derogation should be limited to out-of-market emergency conditions
EEB | 8 | 10 |  |  |  |  | Scope | 746 | Keep the sentence : "Where emission levels associated with the best available techniques (BAT-AELs) are given for different averaging periods, all of those BAT-AELs apply. "We strongly object the deletion. Keeping this sentence is absolutely needed for implementation purposes. | Keep the sentence : "Where emission levels associated with the best available techniques (BAT-AELs) are given for different averaging periods, all of those BAT-AELs apply. " | This provision is to be kept for implementation purposes and effectiveness of the revised BAT-C. The EEB has focussed on the BAT-AEL referred to as yearly averages and we cannot accept that competent authorities can choose to ignore these by complying with the higher / more laxist daily averaged BAT-AEL ranges instead· It has been a common understanding by TWG members that both averaging periods apply, we cannot accept this sudden change of approach. More clarity is always welcome when the objective is to promote harmonised implementation and prevent exploitation of vagueness on how BAT-C need to be implemented. The removal of this important statement is just serving those parties that exploit flexibility in order to downgrade environmental standards·
EEB | 9 | 10 | 2 | 1 | 4 |  |  | 772 | We object to the change made by the EIPPCB which is alterning the substance (scope) of the relaxation | Amend to : "In the case of FBC district heating plants <300MWth combusting fuels with a chlorine content of >1000mg/kg(dry) operated <1500h/yr , the higher end of he range may be up to 20mg/Nm³. The lower end is achievable with wet FGD." | The change is beyond the remit of the EIPPCB to change for consistency without alterning the substance of the BAT-Conclusions. The new change is no longer making the HCL relaxation subject to cumulative 3 conditions (i.e. CFB boiler that fires fuel with a chlorine content of >1000mg/kg (dry and operates less than 1500hours/year). Contrary to what is claimed by the EIPPCB the scope of the relaxation is thus altereed in its practical effect. The BAT conclusions should always be focused on environmental performance outcomes. Specific boiler types / existing configurations should not get much more laxist requirements for the combustion of the same type of fuels. If not mistaken the request for a relaxation was limited to a couple of Polish CFB district heating plants of a size of <300MWth. This size restriction is to be added to be consistent with the outcome of the Final TWG meeting.
EEB | 10 | 10 | 2 | 2 | 3 |  |  | 775 | We object to the change made by the EIPPCB which is alterning the substance (scope) of the relaxation | Keep the old text or replace "For plants burning fuels where the average […] " by "For plants burning only fuels where the potassium content is […]" | The change is beyond the remit of the EIPPCB to change for consistency without alterning the substance of the BAT-Conclusions. The new change is no longer making the NOx relaxation subject to the condition that fuels individually exceed a certain high alaklinity level. There was an agreement at the Final meeting to define "high alkaline content" as >200mg/kg dry for K and/or 300mg/kg dry for Na (see consolidated conclusions page 205). It was however very clear that the footnote relaxations may only be relied on if the plant is ONLY burning high alkali fuels, not if the average of mixed fuels are exceeding the levels. This means that only in case of a single fuel use, due to local availability constraints, that has a high alkalinity level such as straw, the relaxation may be relied on. However that should not be allowed in case of fuel blending.
EEB | 11 | 10 | 3 | 1 | 2 |  |  | 781 | We strongly object to the change made by the EIPPCB which is alterning the substance (scope) of the relaxation | Keep the old text with explicit limitation to the 100-500MWth or delete the whole footnote (preferred option). | Same as comment #4. The change is beyond the remit of the EIPPCB to change for consistency without alterning the substance of the BAT-Conclusions. The new change (removing the size limit of 500MWth) is arbitrarily extending a relaxation clause to prevent secondary NOx abatement also to the largest LCP size group. This extension has not been agreed at the Final TWG meeting. Consistency needs to be ensured vis à vis the BREF aims and objectives and the BREF review rule. Since when do BAT-AEL have to be "consistent" in the sense of aligning to the lowest common denominator that have been politically agreed in the IED? The added value of the BAT conclusions to the IED ELVs are seriously put into question. There is no link to sound technico-economic information and applicability restrictions in BAT 32, rather the contrary. An applicability restriction is available only for the <100MWth size group.
EEB | 12 | 5 | 1 | 3 | 6 | 1 |  | 448 | The emission levels provided give a wrong picture for Oak Grove. | Change: "Emissions data from 2012-2014 indicates that Oak Grove has consistently achieved a level of 60mg/NM³ through retrofitting with SCR and one pulverised unit sized 556 MWe at Sandow retrofitted with SCR in 2009, showed stable yearly average levels of NOX emissions of about 80–90 mg/Nm3. | See EEB submissions in BATIS. CEMs data suggests that the yearly average emissions of Oak Grove are at 60mg/Nm³ . It is important that these levels are reported in the main text
EEB | 13 | [6 empty] | 448 | Provide important background information on NOx levels achieved with SCR by Sostanj 6 (lignite PC) | Add: the following "In Europe, a new 600MWe lignite-fired plant put in operating in March 2015 in Slovenia at Solstanj (unit 6) is fitted with SCR and achieved NOx emission levels of 46mg/Nm³ (daily averaged) . | See EEB submissions in BATIS (31/05/2016). It is important that these levels are reported in the main text of the BREF, so important information is lost. This is especially true because it is the only EU lignite plant with SCR which entered into commercial operation since MArch 2015. The information is raw CEMs data which is validated. The fact that this information dates April 2015 and has been supplied in May is irrelevant since it relates to the "new plants" only, so plants that would be built after the LCP BAT-C publication date (Q1/2017 at the earlierst).
EEB | 14 | 10 | 2 | 1 | 3 |  |  | 769 | Footnote 7: This derogation as written is arbitrary and not based on sound technico economic facts (see comment #6). Referring to pre 1987 plants for a defining state of the art performance as from 2021 is not acceptable. Rather this compromise proposes that the coal/lignite plants (irrespective of size class) may benefit from a relaxation in exchange of reduced operation and commitment to shut by 2024. The 2024 date corresponds to the end date of the Limited Lifetime Derogation (31.12.2023) and decisions taken at national level for phase out e.g. UK and Germany for the lignite reserve ending on 30 September 2023. We are aware that plants currently in the TNP may benefit from this derogation during the July 2020-2024 period. | Footnote 7: Option 3 (backup compromise): amend as follows: "In the case of plants put into operation no later than 1 July 1987, which are operated <1500h/yr and will stop operating by 2024 and for which SCR and/or SNCR is not applicable, the higher end of the range is 340mg/Nm3. | Our preferred approach is full deletion of the footnote as explained in comment 6. However it seems that the original intention by the author (UK) was to allow for the UK plants to keep the current emission levels for the hardcoal PC plants up to the coal phase out date decided for 2024. In any case referring to pre 1987 plants for defining 'state of the art performance' as from 2021 is not acceptable, the aim and integrity of the BREFs need to be preserved. This formulation proposes as a compromise that the intentions of relaxation are kept provided the overall environmenta benefit is preserved, which is not the case for the current proposal which allows indefinite dergoations for plants that could be then over 36 years old!. Those coal/lignite plants (irrespective of size class) may benefit from a relaxation for NOx in exchage of reduced operation and firm commitment to shut by 2024. The 2024 date corresponds to the end date of the Limited Lifetime Derogation (31.12.2023) and decisions taken at national level for phase out e.g. UK and Germany for the lignite reserve ending on 30 September 2023. We are aware that plants currently in the TNP may benefit from this derogation during the July 2020-2024 period. Considering the trade off implications we think this approach is acceptable for the environmental impacts and could support an orderly managed transition to coal phase.
EEB | 15 | 10 | 1 | 3 |  |  |  | 756 | BAT 4 b: we reject the additions by the EIPPCB which are further weakening the BAT conclusion on "fuel choice" applicability restriction. The new wording was not agreed at the Final TWG. Alternative is to restrict clearly for combustion of process fuels in industrial sites where process fuels are generated | BAT4 b: remove the additional words added by EIPPCB and keep text as agreed at the Final TWG meeting. I.e. remove "suitable" and remove "or by the integrated site's fuel balance" . Second option (compromise) "or by the integrated site's fuel balance in case of combustion of industrial process fuels generated at industrial sites" | The EIPPCB has unilaterally decided to change the wording of the BAT conclusions text in order to weaken it further, without any discussion at the Final TWG meeting. The argument is "accidentally forgotten" to include from a Background Document. We strongly oppose this sort of move due to procedureal reasons. Secondly the meaning of "integrated site's fuel balance" is very vague and weakens the BAT on fuel choice even further because it inserts another applicability restriction which is very broad. Finally the reference to "integrated site's fuel balance" was requested by CEFIC comment 86_197 + EUROFER and only related to industrial sites where process fuels are generated (see BP page 284 and point3.1 in page 283)
EEB | 16 | 1 | 3 | 7 |  |  |  | 137 | add in this section interesting information on what implementing stricter BAT levels concretely means also in terms of health protection | Add: The May 2015 Study “Health and Economic implications of alternative Emission Limits for coal fired power plants in Europe” of the European Environmental Bureau and Greenpeace have quantified the damage to health and the environment associated with the emissions from 290 LCPs combusting coal and lignite, and compared these with two scenarios : the proposed upper end BAT-AELs of the LCP draft version of April 2015 and the lower BAT ranges proposed. The study quantified the health implications of either of those scenarios. The main findings are that 71,000 preventable deaths across Europe, due to increased risk of stroke, heart disease, asthma and other illnesses associated with air pollution could be prevented. The loss of life and quality of life, additional drain on health services and the loss of over 23 million working days would cost Europeans over €52 billion between 2020 and 2029. The full study is available here http://www.eeb.org/index.cfm/library/eu-health-impacts-technical-report/ | The study has been supplied in advance of the Final TWG meeting (uloaded to BATIS on 25/05/2015 and summied also as Background information in our written comments) and therfore forms part of material supplied under the information exchange for the LCP BREF. This background information on potential benefits for human health and the environment due to more ambitious implementation of mitigation measures should be added in this section.
EEB | 17 | 10 | [5 empty] | 742 | Add a clear cut off date to establish what a "new" FGD system is. This date should be linked to the dates of the reference plants on which the upper BAT-AEL range has been determined upon. | Change to: Either a flue-gas desulphurisation (FGD) system in a new plant that was commissioned after 2001 or upgraded after 2009 or a FGD system which includes at least one abatement technique introduced or completely replaced in an existing plant following the publication of these BAT conclusions | See comment #1 on implications of definitions. BAT determination should be connected to technical arguments such as performance linked to the abatment equipment on which the information is based on. In this case the age or date of retrofits of wetFGD systems of the reference plants #170 (Megapolis) and #23 Tucimice which were the reference plants for determining the upper BAT-AEL range for SO2. These are both existing FGD systems which reach the upper emission level and combust lignite with Sulphur content up to 3.22% dry/dry. #23Tusimice is a plant that went into operation in 2009 and reached average SOx emissions of106mg/:Nm³ . Reference plant #170 Megapolis IV reached average SOx emissions of 120mg/Nm³ and was commissioned in 1991, the wetFGD system was constructed 10 years after i.e. in 2001. The EEB rejects this desulphurisation rate derogaiton for the worst type of fuels. SOx emissions need to be prevented to the levels that are technically feasible to achieve.
DO NOT insert empty lines (i.e. with no comments). DELETE any empty lines below your last comment.
Note on A2: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B2: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C2: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D2: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E2: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F2: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G2: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H2: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I2: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J2: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K2: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A3: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B3: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C3: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D3: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E3: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F3: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G3: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H3: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I3: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J3: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K3: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A4: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B4: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C4: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D4: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E4: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F4: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G4: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H4: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I4: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J4: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K4: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A5: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B5: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C5: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D5: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E5: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F5: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G5: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H5: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I5: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J5: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K5: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A6: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B6: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C6: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D6: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E6: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F6: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G6: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H6: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I6: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J6: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K6: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A7: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B7: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C7: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D7: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E7: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F7: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G7: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H7: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I7: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J7: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K7: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on N7: EIPPCB: Insert the rationale for the comment
Note on A8: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B8: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C8: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D8: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E8: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F8: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G8: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H8: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I8: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J8: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K8: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A9: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B9: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C9: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D9: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E9: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F9: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G9: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H9: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I9: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J9: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K9: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A13: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B13: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C13: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D13: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E13: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F13: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G13: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H13: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I13: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J13: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K13: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A14: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B14: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C14: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D14: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E14: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F14: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G14: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H14: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I14: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J14: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K14: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A15: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B15: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C15: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D15: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E15: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F15: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G15: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H15: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I15: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J15: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K15: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A16: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B16: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C16: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D16: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E16: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F16: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G16: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H16: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I16: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J16: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K16: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A17: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B17: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C17: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D17: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E17: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F17: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G17: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H17: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I17: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J17: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K17: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)
Note on A18: EIPPCB: Insert the name of your organisation or Member State: e.g.: Finland, CEFIC
Note on B18: EIPPCB: Number each of your comments (use a different number for each comment) e.g.: 1.
Note on C18: EIPPCB: Indicate the first digit of the section or chapter number (if available), e.g. 4, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on D18: EIPPCB: Indicate the second digit of the section or chapter number, e.g. 5, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on E18: EIPPCB: Indicate the third digit of the section or chapter, e.g. 6, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on F18: EIPPCB: Indicate the fourth digit of the Section or Chapter, e.g. 7, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on G18: EIPPCB: Indicate the fifth digit of the section or chapter number, e.g. 8, if the comment relates to Section 4.5.6.7.8.9. If there is no Section or Chapter number leave blank
Note on H18: EIPPCB: Indicate the sixth digit of the section or chapter number, e.g. 9, if the comment relates to Section 4.5.6.7.8.9. If there is no section or chapter number leave blank
Note on I18: EIPPCB: Indicate the seventh digit of the section or chapter number, e.g. 3, if the comment relates to Section 4.5.6.7.8.9.3 If there is no section or chapter number leave blank
Note on J18: EIPPCB: Select one of the options from the drop-down list to indicate the title of the chapter your comment refers to: e.g.: Preface This field is to be left empty if there is a section or chapter number the comment refers to
Note on K18: EIPPCB: Indicate the page number your comment refers to: e.g.: vi (if the comment is on page vi of the Preface) or 45 (if the comment is on p.45 of the PDF version of the BREF)