BREF BAT Candidate

Gore Mercury Control System

SECTOR: Large Combustion PLants

Ole Petzoldt, W.L. Gore & Associates
Email: opetzold@wlgore.com

Putzbrunn/Germany, 17 April 2015

# Gore Mercury Control System

## Description

The GORE® Mercury Control System (GMCS) is based on a novel, fluoropolymer-based Sorbent Polymer Composite (SPC) material (Fig. 1) which efficiently removes both elemental and oxidized mercury from the flue gas stream. As such, it is insensitive to fuel or process changes that affect mercury speciation. Mercury is strongly bound within the SPC which has a high capacity for mercury storage allowing for long life without the need for regeneration. The SPC can operate even in very wet gas streams, making it ideal for location above the mist eliminators in a wet FGD system. The removal of SO2 is a co-benefit as it is converted to sulfuric acid which is expelled out of the hydrophobic SPC material into the absorber vessel below (Figure 2). When installed in a scrubber the GMCS serves as a barrier to mercury reemissions, since it is located at the outlet of the scrubber and effectively removes elemental mercury. This allows a plant to avoid the need for re-emissions additives, and focus the scrubber operation on avoiding other unwanted problems like selenate formation. Unlike many activated carbon sorbents, the presence of SO3 does not inhibit mercury capture by the SPC, making it a very effective solution for high sulfur coals or units with SO3 gas conditioning.

Operation is passive. There are no moving parts and adjustments are not needed to maintain performance as unit operations change. Since there are no injected sorbents, there is absolutely no concern over fly ash contamination or creating additional particulate matter that needs to be collected.

Chemicals for oxidation are also not needed thus eliminating halogen-induced corrosion concerns or wastewater treatment complications. The GMCS is modular in design with the SPC material arranged in open channels for low pressure drop. The modules are resistant to fouling or plugging, in part due to the smooth, non-stick nature of the SPC, and in part due to the continual acid wash created by the conversion of SO2 to liquid sulfuric acid. The modules can be stacked in the direction of gas flow to achieve the desired mercury removal efficiency.

Figure 1: Gore Mercury Control System in a wet FGD scrubber

Figure 2: Construction of the Sorbent Polymer Composite

The GMCS can be designed to achieve required mercury removal efficiency approaching or exceeding 90% depending on the number of modules and gas velocity (Figure 3).

Figure 3: Stacked Modules Design for Desired Removal Efficiency

A GMCS installed within a scrubber absorber requires no additional footprint thus minimizing capital costs. The system is also very cost-effective to operate with module replacement required only on a very infrequent basis.

## Environmental Benefit

Gore Mercury Control System captures elemental and oxidized mercury, does not require additives or chemicals and does not transfer mercury into the waste water or gypsum. It is insensitive to common sorbent poisons (SO3, VOCs) and can be installed in existing wet FGD scrubbers.

## Operational Data

In July 2013, a full scale 75 MW system was installed in one scrubber at Xcel’s Sherburne County (Sherco) plant in Minnesota, and operated for ~5 months. The system achieved an average of 60-70 % efficiency.

Figure 4 shows mercury inlet and outlet concentrations at Sherco.

Figure 4: GMCS Inlet and Outlet Hg Concentration at Sherco

In June of 2014, a full-scale commercial 550MW system was installed at a confidential site in the Eastern U.S.. This site has operated continuously since installation and will reach one year of operation this summer.

In October of 2014, a full-scale commercial 160 MW system was installed at Cayuga Operating Company’s Cayuga plant in New York. This plant operates this unit based on demand, and is subject to a more stringent state limit of 0.6 lb Hg /TBtu, which took effect on January 1, 2015. Typical uncontrolled Hg levels at the stack (prior to installation of the GMCS) are in excess of 2 lb/TBtu. The plant has been in compliance since start-up of the GMCS, with typical outlet mercury readings around 0.3 lb Hg/TBtu. See Figure 5.

FIGURE 5

Figure 5: Outlet concentrations measured at Cayuga Operating Company via sorbent traps at the outlet of the Gore Modules.

In coal-fired power, another full-scale commercial installation sized at 450MW will be starting up in May of 2015 – construction is nearly complete and modules have been delivered. This will bring the installed capacity up to over 1000 MW. Two more large full-scale commercial units will start up in early 2016 (contracts are already signed and design work is underway), so that by the summer of 2016, the installed capacity will be approximately 2100 MW.

Pressure drop of the Gore Mercury Control System is less than 400 Pa. (The pressure drop through a single module layer is approximately 60 Pa at a gas velocity of 4 m/s.).

The SPC can retain over 5% of its weight in mercury without a drop in removal efficiency, equating to 1 to 2 tons of mercury holding capacity for a 1000 MW plant (see figure 6). As a result, the projected module lifetime for most power plants is around 10 years, based on the average mercury concentration in the flue gas after a wet scrubber.

Figure 6: Hg Efficiency as a function of SPC Hg Capacity

## Cross-media effects

Mercury is not shifted from flue gas to waste water, gypsum or any other media. The Gore modules are the sink for the captured mercury.

When the modules have reached end-of-life, the SPC material can be removed for disposal while the housing can be reused. Options for material disposal include landfill in an approved hazardous waste landfill or sending to a retort facility for mercury removal and disposal in a non-hazardous landfill. The quantity of SPC material that needs to be disposed of at the module end-of-life is at least several orders of magnitude smaller than the quantity of injected sorbents that would be used to control mercury with a sorbent injection system for the same period of time. As a result, the disposal costs are typically considerably lower than with competing approaches for mercury control.

## Applicability

The Gore modules can be located in a wet FGD system above (downstream of) the mist eliminators where they can be an effective barrier to mercury re-emissions from the scrubber. If mist eliminators do not leave sufficient room above for installing the GMCS, they can be reconfigured and lowered so as to provide sufficient room for module installation.

For plants that do not have wet FGDs installed, this technology can be applied after a dry scrubber, or even as a stand-alone solution for mercury and SOx. Depending on the application, an evaporative cooler may be installed upstream of the Gore Modules to cool the gas stream to around 85 °C for maximum effectiveness. Although these non-wet FGD installations require a separate structure to house the modules, which increases capital costs and space requirements, many of the other advantages are maintained. The GMCS has been successfully tested in various other applications such as mercury removal from cement kiln flue gas, and is being considered for a wide variety of industrial applications beyond coal-fired power plants.

In addition to coal-fired power applications, several full-scale installations in sewage sludge incinerators are under way and will start-up before spring 2016. Although the application is different, the installation approach is similar, with several layers of modules being placed at the outlet of the wet venturi scrubber providing the necessary mercury control to achieve compliance. These applications have higher mercury concentrations and smaller gas flow rates compared to coal fired power, but the modules function in the same fashion.

## Economics

Gore has conducted several dozen system designs for U.S. power plants in which the capital and operating costs are compared to various alternative approaches such as carbon injection or calcium bromide coal additives. In nearly all cases evaluated, the GMCS can be installed in the existing wFGD, and the GMCS approach offers compelling economic advantages over the alternatives being considered by those plants. In particular, the operating costs of the GMCS tend to be very low, and the risk of certain unintended consequences (lost fly ash sales, bromine induced corrosion) is eliminated. Since the economics are typically fairly site-specific, it is recommended that interested plants contact Gore and provide some specific plant information in order for a more accurate cost projection to be provided. Figure 7 shows a typical cost comparison.

Figure 7 Cost Comparison of Gore Technology with Other Mercury Control Technologies (Power)

## Summary of Benefits of GORE™ Mercury Control System

Low Impact

Requires no carbon injection with no concerns about resulting fly ash contamination or additional particulate loading

Requires no bromine injection eliminating corrosion and wastewater concerns

Low Maintenance

Has no moving parts

Does not require adjustments to maintain mercury removal

Does not need regeneration

Robust Performance

Removes elemental and oxidized mercury species with equal effectiveness

Is insensitive to SO3

Provides re-emissions barrier when installed in a wet FGD absorber

Cost Effective

Has long module lifetime

Demonstrates low operating cost

Has a zero footprint in a wet FGD absorber

Removes SO2 as a co-benefit

Mercury Removal Guaranteed

## Driving Force for Implementation

Legal requirements

## Reference Plants

- Xcel Sherburne County

Coal-fired power plant, Minnesota

Single Absorber, ~75 MW

July – December 2013

- Confidential Site

Coal-fired power plant, U.S.

550 MW Absorber

Operating continuously since June 2014

- Cayuga Operating Company

Coal-fired power plant, New York

Single Absorber, ~160MW

Started up and operated intermittently since Oct 2014

- Confidential Site

Coal-fired power plant, U.S.

Two Units, ~450MW each

Fabrication underway

First Unit start-up May 2015, second unit start-up May 2016

- Confidential Site

Coal-fired power plant, U.S.

550MW Absorber

Scheduled start-up April 2016

## Reference Literature

- Klingspor, Jonas (AECOM), Roll, Douglass (Cayuga Operating Company), Kolde, Jeff (W.L. Gore). “Installation of a Gore Mercury Control System at Cayuga”, EUEC conference in San Diego, Feb 17, 2015

- Klingspor, Jonas (URS), Kolde, Jeff (W.L. Gore). “URS/Gore: Gore Mercury Control System”, Reinhold APC Conference in Louisville KY, July 15, 2014

- Kolde, Jeff (W.L. Gore) et al, Machalek, Tom (URS) et al, Henningsgaard, Robert (Xcel Energy), Pazarsky, Jaren (Great River Energy) et al, Chang,Ramsay (EPRI). “Field Results of Fixed Structure Sorbent Technology for Mercury Reduction”, PowerGen conference in Orlando, Nov 13, 2013